## Slide 1
QUANTITY OF WATER
Source: sprin.org
Group Members:
Pradeep, 103
Pragyan, 104
Prajwal , 105
Prakash, 106
Pramod, 107
Pranish , 108
Tutor:
Asst.Prof. Shukra Raj Poudel
Department of
Civil Engineering
IOE, Tribhuvan University
Dec 26, 2019

## Slide 2
Objectives of the Presentation
Students will be able to learn the following things:
Various types of water demand of the community
The factors affecting water demand
Estimation of water demand
Necessity of population forecasting and its methods

## Slide 3: Presentation Outline
3.0 Introduction
3.1 Per capita demand of water
3.2 Base and design periods
3.3 Types of water demand
3.4 Variation in demand of water
3.5 Peak factor
3.6 Factors affecting demand of water
3.7 Population forecasting
3.8 Numerical on population forecasting and water demands

## Slide 4: 3.0 Introduction:
The first step in the design of water supply system of a community is the determination of the quantity of water required in the community for various purposes.
Quantity of water will determine the sizes and capacities of all the components of water supply system such as intake chamber, transmission main, water treatment units, reservoir, distribution system, etc.
Estimation of the quantity of water (or, water demand) requires the following three factors to be known:
  Per capita demand of water or rate of demand
  Base and design period
  Population

## Slide 5: 3.1 Per capita demand of water
The average quantity of water consumption or water demand for various purposes per person per day is known as per capita demand or water.
It is usually expressed in liters per capita per day (lpcd).
The per capita demand of water may vary according to the lifestyle of people and the development of community. Water demand in l/d = Per capita demand x Population

## Slide 6: 3.2 Base and design periods
Base Period
It is the period required for the survey, design and construction of a water supply system.
Normally, It spans for 2 to 3 years of time for a water supply system.
Design Period
Generally water system projects are designed for a design period of 20 to 40 years.
Different segments of the water treatment and distribution systems may be approximately designed for differing periods of time using differing capacity criteria, so that expenditure far ahead of utility is avoided.

## Slide 7: 3.2.1 Typical Base and Design Periods
Community | Base Period (Years) | Design Period (Years)
Rural water supply system with low population growth rate | 2-3 | 20
Rural water supply system with high population growth rate | 2-3 | 15
Urban water supply system | 2-3 | Up to 30
Water Supply Engineering
Prof. Dr. Bhagwan Ratna Kansakar
Generally adopted in Nepal:

## Slide 8: 3.2.2 Selection basis of Design Period
Population growth rate
Development of community
Useful life of component structures
Availability of funds
Rate of interest on borrowings
Availability of water at source

## Slide 9: 3.2.2 Selection basis of Design Period
Population Growth Rate Higher the population growth rate, shorter the adopted design period.
Development of Community If the community is rapidly developing there will be high population growth rate, so shorter design period is adopted.
Continued…

## Slide 10: 3.2.2 Selection basis of Design Period
Useful Life of Component Structures The useful life of the component structures depends on the quality and type of materials. The design period should not exceed this time period.
Availability of Funds When limited funds are available shorter, design period is adopted, and vice-versa.
Continued…

## Slide 11: 3.2.2 Selection basis of Design Period
Rate of Interest on Borrowings Lower the interest rate, longer the design period can be made.
Availability of Water at Source Shorter design period is adopted if the water available at the source is limited, and vice-versa
Continued…

## Slide 12: 3.2.3 Base and design years
Base Year
It is the year in which water is delivered to the community by a water supply system after the completion of its construction.
Base year = Survey year + Base period where, Base period is usually 2 - 3 years.
Design Year
It is the year upto for which a water supply system is designed.
The sizes and components of all water supply system components are calculated for the design year.
Design year = Base Year + Design Period
Survey Year
+ Base Period
Base Year
+ Design Period
Design Year

## Slide 13: 3.3 Types of Demand
Engineeringnotes.com
alamy.com
Indiamart.com
dreamstime.com
archive.swmm.info
www.alamy.com
3.3.1 Domestic Demand
3.3.2 Livestock Demand
3.3.3 Commercial Demand
3.3.4 Public/Municipal Demand
3.3.5 Industrial Demand
3.3.6 Fire Demand
3.3.7 Loss and Wastage
3.3.8 Total Water Demand

## Slide 14: 3.3.1 Domestic Demand
It includes the water which is required for use in a private residence, apartment, houses for drinking, cooking, sanitary purpose, etc..
This demand depends on the living standard of people.
The domestic water demand in Nepal is generally taken as follows:-
Type of house | Requirement (lpcd)
Fully plumbed house | 112lpcd
Partly plumbed house | 65lpcd
Rural area served by public stand post | 45lpcd
Water Supply Engineering
Prof. Dr. Bhagwan Ratna Kansakar

## Slide 15: 3.3.2 Livestock Demand
It includes the water consumed by domesticated animals like horses, cows, pigs, etc.
The quantity of water depends upon the type and size of animals.
Livestock demands in Nepal are generally taken as follows:
Animals | lpcd (liters/animal/day)
Cows, buffalo, horse | 45 lpcd
Pigs, Sheep, Goats, | 20 lpcd
Chickens, ducks | .2
Water Supply Engineering
Prof. Dr. Bhagwan Ratna Kansakar

## Slide 16: 3.3.2 Livestock Demand
Livestock demand will not solely depend on the water supply system. Many Livestock's will utilize natural rivers, streams, and ponds for the water during the grazing. Thus, livestock demand should not be more than 20% of domestic demand. So, in the rural area, this factor must be included and in the urban area, it can be neglected.
Continued…
www.alamy.com

## Slide 17: 3.3.3 Commercial Demand
This includes the water demand for commercial establishments such as educational institutions, offices, hotels, hospitals, restaurants, etc.
The quantity depends on the type of commercial establishment. It must be taken into account.
mountainwater.com.au

## Slide 18: 3.3.3 Commercial Demand
S.N. | Commercial Establishment | Water Demand
1 | Day-scholars in educational institutions | 10 liters/pupil/day
2 | Boarders in educational institutions | 65 liters/pupil/day
3 | Offices(depending upon size) | 500-100 liters/day
4 | Hospitals with bed | 500 liters/bed/day
5 | Hospitals without bed and health clinics | 2500 liters/day
6 | Hotels with bed | 200 liters/bed/day
7 | Hotels without bed | 500-100 liters/day
8 | Restaurants and tea stalls | 500-1000liters/day
Continued…

## Slide 19: 3.3.4 Public/Municipal Demand
This includes the quantity of water required for public or municipal utility purposes such as watering of public parks, sanitary purposes (road washing,..).
A provision of 5 to 10% of the total consumption is made for these demands.
This demand is taken into account only in the urban community only.

## Slide 20
3.3.5 Industrial Demand
This includes water for industrial purposes.
The presence of industries shows a greater impact on water demand.
For a city with moderate factories, a provision of 20 to 25 percent of total consumption may be made for the purpose only in urban.

## Slide 21: 3.3.6 Fire demand
It is the quantity of water required for fire fighting purposes.
In a thickly populated area, fire may break out and may result in severe damages.
Various schemes for fire demand estimation are:
Formula Name | Formula (P in 1000s)
Indian Water Supply Manual and Treatment Formula | Q=100√P
2. Buston’s Formula | Q=5663√P
3. Kuichling’s Formula | Q=3182√P
4. Freeman’s Formula | Q=1136(
5. National Board of Fire Under water's Formula | Q=4637√p(1-.01√P)
Formula Name | Formula (P in 1000s)
Indian Water Supply Manual and Treatment Formula | Q=100√P
2. Buston’s Formula | Q=5663√P
3. Kuichling’s Formula | Q=3182√P
4. Freeman’s Formula | 
5. National Board of Fire Under water's Formula | Q=4637√p(1-.01√P)

## Slide 22: 3.3.7 Loss and Wastage
This includes the losses of water due to leakage in main veins, valves, and other fitting, worn or damaged meters, theft of water and other reasons.
In the case of well maintained and fully metered water distribution system, the losses hardly exceed 15% of the total supply.
And in the system where there is a weak management system, there may be a loss of water up to 50 % of the total supply.

## Slide 23: 3.3.8 Total Water Demand
TWD
=DD + LD + CD + PD + ID + FD+ LW
Where,
TWD = Total Water Demand
DD = Domestic demand
LD = Livestock Demand
CD = Commercial Demand
PD = Public/municipal Demand
ID = Industrial Demand
FD = Fire Demand
LW = Loss and Wastage

## Slide 24: 3.4 Variation in Water Demands and Parameters

## Slide 25: 3.4 Variation in Water Demands and Parameters
  Hourly Variations in Water Demand
Continued…
Water Supply Engineering
Prof. Dr. Bhagwan Ratna Kansakar

## Slide 26: 3.6 Factors Affecting Demand of Water
Climatic condition:
Requirement is more at places having hot and dry climate than at places having cold and humid climate. More water is consumed during summer. In extremely cold climates, water may be wasted due to taps being always kept open to avoid freezing of pipes, which may result in increased rate of consumption
Cost of water:
The rate at which water is supplied to the public affects the demand of it. If the rates at which water is supplied are high, lesser quantity of water may be consumed by the people, and vice versa.

## Slide 27: 3.6 Factors Affecting Demand of Water
Pressure in Distribution System
At high distribution pressure, there is increase in loss and waste of water.
Method of Charging- Metered or Unmetered:
Metered water supply system means that meters are fitted at the head of individual household connections, which record the quantity of water consumed. As with metered system, consumers become more conscious about the usage to reduce the water bills whereas in unmetered households, consumers use water more liberally and water demand increases significantly.
Continued…

## Slide 28: 3.6 Factors Affecting Demand of Water
Number of Commercial Establishments and Industries:
The rate of demand would increase drastically where there is presence of commercial establishments and industries as they consume significantly high water compared to that of regular households.
Sewerage System:
A town with good sewerage system has high demand of water. More water is consumed for flushing sanitary units such as urinals, water closets, etc.
Continued…

## Slide 29: 3.5 Peak Factor
It is the ratio of maximum or peak demand of water to that of the average annual demand for water.
Max demand or peak demand = peak factor * annual average demand
Or, Peak factor = seasonal peak factor * daily peak factor * hourly peak factor
The peak factor of 2 to 4 is adopted in Nepal for a continuous system of supply.

## Slide 30: 3.7 Population Forecasting
Population of an area keeps changing and generally it increases with time.
It is necessary to estimate future population for the end of service.
The information of population of city or village of nepal can be obtained from census data
Various methods are available for population forecasting and designers should choose the suitable methods among them.

## Slide 31
Methods of Population Forecasting:
Simple Graphical Method
05
Simple graph is used
Decreasing Rate Method
04
Geometric Increase Method
02
Arithmetic Increase Method
01
P’=P+I*n
Methods of Population Forecasting
Master Plan Method
08
Cities are divided into small parts
Comparative Graphical Method
06
Population of different cities is used
Incremental Increase Method
03

## Slide 32: 01. Arithmetic Increase Method
Rate of change of population per time unit say ‘I’ remains constant
dp/dt=constant
Then,
Generalizing,
Where,
Pn=future population after n decades
P=latest population
I=Average increase in population per decades

## Slide 33: 02. Geometric Increase Method
Percentage increase in population per decade is assumed to be constant
Future population is given by:
1+
Where,
Pn=future population after n decades
r= average percent increase in population
P=latest population
}
}
After one decade
After two decades

## Slide 34: 03. Incremental Increase Method
Improvement over Arithmetic and Geometric Method seems to be combination of them
The increment in increase in population is called incremental increase
It may be positive and negative
Future population is given by:
Where,
Pn = Future population after n decades
P = latest population
I = Average increase in population per decade
x = Average Incremental increase in population per decade

## Slide 35: 04. Decreasing Rate of Growth or Changing Rate of Growth Method
Rate of change of increase in population is assumed to be constant
dr/dt=constant
Then,
Generalizing

## Slide 36: Continued...
Where,
Pn= Future population after n decade
P = Latest population
r = Percentage increase in population of last decade
r’ = Average decrease in rate of increase in population per decade

## Slide 37: 05. Simple Graphical Method

## Slide 38: 06. Comparative Graphical Method

## Slide 39: 3.8 Numerical Example of Population Forecasting:
Determine the population of the town in the year 2088 and 2084 by
a) Arithmetical Increase Method
b) Geometrical Increase Method
c) Incremental Increase Method
d) Decreased rate of Growth Method
The census population of the city is given as follows:
IOE 2072 Kartik
Year | 2068 | 2058 | 2048 | 2038 | 2028
Population | 65,500 | 57,000 | 47,000 | 37,000 | 29,000

## Slide 40: Solution:
Year | Population | Increase in Population | Incremental Increase | % Increase in Population | Decrease in % Increase In Population
2028 | 29,000 | - | - | - | -
2038 | 37,000 | 8,000 | - | 27.586 | -
2048 | 47,000 | 10,000 | 2,000 | 27.027 | 0.559
2058 | 57,000 | 10,000 | 0 | 21.277 | 5.75
2068 | 65,500 | 8,500 | -1,500 | 14.912 | 6.365
Total: |  | 36,500 | 500 | 90.802 | 12.674
Average: |  | 9125 | 166.667 | 22.701 | 4.225
37,000
29,000
-
=
8,000
10,000
8,000
2,000

## Slide 41: Solution:
Year | Population | Increase in Population | Incremental Increase | % Increase in Population | Decrease in % Increase In Population
2028 | 29,000 | - | - | - | -
2038 | 37,000 | 8,000 | - | 27.586 | -
2048 | 47,000 | 10,000 | 2,000 | 27.027 | 0.559
2058 | 57,000 | 10,000 | 0 | 21.277 | 5.75
2068 | 65,500 | 8,500 | -1,500 | 14.912 | 6.365
Total: |  | 36,500 | 500 | 90.802 | 12.674
Average: |  | 9125 | 166.667 | 22.701 | 4.225
-
=
8,000
/
29,000
*100%
27.586
27.586
27.027
0.559

## Slide 42
From table:
P=65,500 I=9,125 x=166.667 r=22.701% r’=4.225%
1. Arithmetical Method
Pn = P+nI
2. Geometrical Method
Continued…

## Slide 43
03. Incremental Increase Method
04. Deceased Rate of Growth Method
0.6
Continued…

## Slide 44: Numerical Problem on Population on Population forecasting and water Demand
Data obtained from a baseline survey of newly formed municipality in year 2016 AD are as follows:
Survey year | 2013 | Annual Growth Rate | 1.5%
Base period | 3 years | Day Scholar Student | 100
Design period | 25 years | Boarder scholar students | 10
Population | 1250 | No. of Health Post | 1
Cows | 200 | No. of Tea Shop | 1
Goats | 500 | No. of VDC Office | 1
Chicken | 5000 |  | 
Calculate average water demand for design year. IOE 2073 Chaitra

## Slide 45: Solution:
Here,
Survey year = 2013
Base period = 3 years
Design period = 25 years
Total Design period = base period + design period
= 3 +25 = 28 years
Survey year population (P) = 1250
Survey year Day scholar students No. = 100
Survey year Boarder students No. = 10
Growth rate per year ( r ) = 1.5%

## Slide 46
Then, for design year
Population ()
No. of day scholar students =
No. of Boarder students =
Calculation of demand:
a) Domestic Demand:
Domestic Demand = 1897 * 45 (lcpd)
= 85365 liter per day
Continued…

## Slide 47
b) Livestock Demand:
Cows= 200 * 45 (lpapd) = 9000 lit per day
Goats= 500 * 20 (lpapd) = 10000 lit per day
Chicken= 5000 *0.2(lpapd) = 1000 lit per day
Total = 20000 lit per day
20% of Domestic demand = 85365 * 20/100
= 17073 lit per day
Here, Livestock demand > 20% of Domestic demand
So, We have to take livestock demand = 20% of DD
=17073 lit per day
c) Institutional Demand or Commercial:
Day scholar student= 152 * 10 (lpppd)=1520 lit per day
Boarder students= 16 * 65 (lpppd)=1040 lit per day
Continued…

## Slide 48
Health post = 1 * 2500 (lpd) = 2500 lit per day
Tea shop = 1 *1000 (lpd) = 1000 lit per day
VDC office = 1*1000 (lpd) = 1000 lit per day
Total Commercial Demand = 7060 lit per day
Hence, total Demand of water for design year is
=Domestic demand+Livestock demand+Commercial demand
= 85365 + 17073 + 7060
= 109498 lit per day
Continued…

## Slide 49
Thank you!